## Slide 1: Petroleum Storage Tank Rule Updates Complying with the new PST rules and changes to the PST Compliance Notebook Trade Fair 2018
Rebekah Stanush
Compliance Assistance Specialist
Austin Central Office
512-239-5834
Rebekah.Stanush@tceq.texas.gov
Rebecca Costigan
Compliance Assistance Specialist
Houston Regional Office
713-767-3693
Rebecca.Costigan@tceq.texas.gov

## Slide 2: New EPA PST Rules
2015 Federal UST Regulations
2018 Texas UST Regulations
Texas adoption of new rules in late May 2018
Notes: This rulemaking incorporated the 2015 Federal UST Regulations into the Texas Administrative Code (Title 30, Chapter 334). The new requirements have been drafted in the proposed rules, but they are not effective yet. We anticipate they will be approved as drafted (not guaranteed). Anticipated effective date is May 31, 2018.
These new rules require UST systems to be maintained in a manner that will prevent releases and minimize impacts to human health and the environment. The EPA estimates that as of 2015, more than 525,000 UST releases have been confirmed in the United States. Regular maintenance is important because it helps ensure timely repair or replacement of components when problems are identified, and helps reduce releases to the environment.

## Slide 3: 2015 UST Federal Regulations
EPA updated the 1988 Regulations
Published in Federal Register July 2015
  Effective in states without SPA
Texas has State Program Approval (SPA)
  Texas must reapply for SPA by October 2018
Notes: The EPA rules became effective in 16 states without State Program Approval (SPA) and Indian country; not yet adopted in Texas. Since Texas has the SPA agreement, we had a delayed implementation deadline for these new rules. To reapply for the SPA agreement, Texas needs to adopt their rules prior to October 2018 deadline to keep the SPA agreement with EPA.

## Slide 4: Current Texas Regulations
Texas meets many of the 2015 Federal regulations
  Operator Training since 2012
  Secondary Containment since 2009
  Emergency Generator Requirements, Airport Hydrant Systems (AHS) and Field Constructed Tanks (FCTs)
  Notification requirements for ownership changes
Notes: Operator training has been required since 2012. Secondary containment has been required since January 1, 2009 for new systems. Removed deferrals for Emergency Power Generators, Airport Hydrant Systems, and Field Constructed Tanks. A Field Constructed Tank is a tank constructed of concrete poured in the field, or steel/FRP that is primarily fabricated in the field- typically bulk USTs. An Airport Hydrant System fuels aircrafts and operates under high pressure with large diameter piping that terminates into one or more hydrants or fill stands. It begins where one fuel sources enters one or more tanks from an external sources (pipeline, barge, rail car). An AHS can have a combination of ASTs and USTs, but if 10% of the system’s total capacity is underground, then it is a UST.
Texas already requires notification of ownership changes.

## Slide 5: Changes to Texas UST Regulations
Walkthrough Inspections
Periodic Testing
Periodic Inspections
Annual Testing
Release Detection every 30 days
Flow Restrictors
Repairs
Used Oil Tanks
E10+ and B20+
Operator Training
Notes: Here is an overview of the requirements that are affected by the rulemaking. For each of these rule changes, we will go through the requirements followed by a discussion of how to comply with the new rule. This presentation serves as a preview to the changes that will be made to the “UST Compliance Notebook for Texas” to incorporate these new requirements after rule adoption.
We’ll also reference EPA guidance that may help you in the meantime while our guidance is being drafted. (Source: Operating And Maintaining Underground Storage Tank Systems- Practical Help And Checklists, EPA 510-K-16-001, February 2016 - https://www.epa.gov/sites/production/files/2016-02/documents/om_final_2-17-16_508_0.pdf). Disclaimer: use caution when using this EPA guidance because it is based on the Federal rules; TCEQ’s rules must be at least as stringent, but the agency can implement rules that are more stringent than the federal rules.

## Slide 6: Walkthrough Inspections
January 1, 2021
Every 30 days
  Spill prevention equipment
  Release detection equipment
Every year
  Sumps
  Hand held release detection equipment
Notes: While we talk about these changes to the Texas UST Rules, please keep in mind that these rules are not published in Texas Register, yet. Therefore, these rules are not yet effective.
By January 1, 2021, you must (1) conduct your first periodic (30-day) operation and maintenance walkthrough inspection of spill prevention and release detection equipment, and (2) conduct your first annual walkthrough inspection of sumps and hand-held release detection equipment.
Spill prevention equipment includes spill buckets, tight fill fitting, spill bucket lid.
Release detection equipment could include ATG, inventory control, SIR, interstitial monitoring, sensors, etc.
Sumps include sumps and manways for motors, under the dispenser, etc.
Hand held release detection includes groundwater and vapor monitoring equipment.

## Slide 7: Walkthrough Inspections
Spill Prevention Equipment
  Every 30 days
  Fill pipe
  Fill cap
  Interstitial area
  Remove debris and liquid within 96 hours
    May accumulate waste material on-site
    Dispose properly
Notes: Spill prevention equipment: a catchment basin, spill bucket, or other spill containment device.
Check for damage, fill pipe obstructions, security of fill cap, and leaks in interstitial area (if applicable: for double-walled spill prevention equipment with interstitial monitoring).
Remove liquid and debris within 96 hours and dispose of properly.
*Exception: spill prevention equipment at systems receiving deliveries more than 30 days apart may be checked prior to each delivery.
Previously, facilities were required to dispose of liquid and debris within 96 hours. This is not feasible as it required facilities to dispose of very small amounts of waste immediately. The new rule requires that liquid/debris be removed within 96 hours, but facilities may accumulate the waste material onsite per the waste rules and properly dispose of it on a more convenient and cost-effective schedule.

## Slide 8: Walkthrough Inspections
Release Detection Equipment
  Every 30 days
  Check for alarms
  Review records
    Release detection testing
    Inventory control
Notes: Check for alarms or unusual operating conditions.
Review release detection testing records.

## Slide 9: Walkthrough Inspections
Sumps
  Every year
  Containment Sumps with Interstitial Monitoring (IM)
    Verify liquid tightness
  All Sumps
    Check for damage, releases, debris, liquid*
    Remove debris and liquid* within 96 hours
    Check cathodic protection (if applicable)
  * Not required to remove liquid if:
    Sump installed before January 1, 2009
    Equipment has cathodic protection
    Sump is uncontained
Notes: Containment sumps installed on or after Jan. 1, 2009 (and all sumps used for interstitial monitoring) are required to be liquid tight.
Check for damage, leaks to containment area, releases, and leaks in interstitial area (if applicable).
Remove liquid* and debris within 96 hours and dispose of properly.
Check for releases, presence of cathodic protection (if contains water that contacts metal components that routinely contain product).
*Not required to remove liquid from sumps (such as the submersible turbine (STP) sump and under dispenser containment (UDC)) during annual inspection if the equipment is cathodically protected, or if the sump is uncontained or installed before 1/1/2009.
For areas with submersible turbine pumps and under-dispenser areas that do not have containment sumps:
Check for damage, releases, presence of cathodic protection (if water, soil, or backfill contacts metal components that routinely contain product).
Remove any debris.

## Slide 10: Walkthrough Inspections
Hand-held release detection equipment
  Every year
  Check for operability
  Examples: tank gauge sticks, groundwater bailers

## Slide 11: Walkthrough Inspections
How do I comply?
  First walkthrough inspection by January 1, 2021
  Records for 5 years
    List of areas checked
    Issues and corrective action
    Delivery records
    Waste manifests
Notes: Keep records for 5 years, including:
- a list of areas checked
- any issues and the corrective action taken
- delivery records to verify infrequent delivery exemption, if applicable
- waste manifest or trip ticket to show proper disposal of liquid removed from spill buckets or sumps
*Temporarily out-of-service UST systems do not require spill and overfill operation and maintenance walkthrough inspection.
Example Walkthrough Inspection Checklist in EPA guidance: https://www.epa.gov/sites/production/files/2016-02/documents/om_final_2-17-16_508_0.pdf - See Page 54: Sample Walkthrough Inspection Checklist

## Slide 12: Periodic Testing
Spill Prevention Equipment & Containment Sumps with IM
  Double-walled
    Monitor integrity during walkthrough inspection
  Or
  Single or double-walled
    Test for liquid tightness every 3 years
Notes: By Jan. 1, 2021, for UST systems in use before Sept. 1, 2018:
Spill prevention equipment (spill buckets) and containment sumps used for interstitial monitoring of piping must be periodically monitored/tested by one of the following:
- If equipment is double-walled, monitor the integrity of both walls at the walkthrough inspection frequency, or
- Test for liquid tightness at least once every 3 years (using vacuum, pressure, or liquid testing).

## Slide 13: Periodic Testing
Wastewater disposal
  Pump and Haul
  Hydrostatic Test Water General Permit (GP)
  Petroleum Fuel or Petroleum Substances GP
    Allowable option after GP is effective (Sept. 2018)
Notes: Triennial Tightness Testing: Wastewater
  3 options for disposing of wastewater generated from this tightness testing:
  1) Pump-and-Haul: capture the test water and dispose of it at an authorized wastewater treatment plant (WWTP) or publicly owned treatment works (POTW). You will need to check with the WWTP/POTW and ask whether they will accept the wastewater.
  2) Hydrostatic Test Water General Permit (TXG670000)
    -Hydrostatic test water from new vessels does not have to meet effluent limits and does not have to be analyzed. The effluent limits and monitoring only apply to existing vessels that previously contained petroleum fuel or petroleum product.
    -The facility owner/operator does not have to submit a notice of intent application to get authorization to discharge hydrostatic test water from new vessels into or adjacent to water in the state. They do have to comply with all other requirements in the permit.
  3) Petroleum Fuel or Petroleum Substances General Permit (TXG830000)
    -Cannot be used to authorize discharge until new GP is effective (Sept. 2018)
    -The UST customer group was added to the draft Petroleum Fuel or Petroleum Substances General Permit (TXG830000); however, this language will not be adopted until the general permit (GP) becomes effective (anticipated 9/12/18). This means PST facilities will not be eligible for the GP from the time the new rules are effective (anticipated 5/31/18) and 9/12/18. This should not adversely impact PST facilities since the sump testing requirements have been in place since 2012, and the new spill bucket testing rules will not be implemented until 2021.
  Liquids used for testing can be reused for subsequent testing (either at the same facility or at other facilities), but the discharge must meet permitted effluent limits or be properly disposed (e.g. pump-and-haul).
  For additional information, see TCEQ webpage “Available Water Quality General Permits”- https://www.tceq.texas.gov/permitting/wastewater/general

## Slide 14: Periodic Testing
How do I comply?
Existing Facilities prior to September 1, 2018:
  Test by January 1, 2021
New facilities on or after September 1, 2018:
  Test when brought into service
Keep test and inspection records for 5 years
Keep test wastewater disposal records
Notes: By Jan. 1, 2021, UST systems in use before Sept. 1, 2018, must conduct periodic monitoring/testing of spill prevention equipment and containment sumps used for interstitial monitoring of piping.
Upon startup, UST systems in use on or after Sept. 1, 2018, must conduct initial periodic monitoring/testing of spill prevention equipment and containment sumps.
Keep records of tests and inspections for five years.
- See EPA guidance Page 32: Checklist For Spill Buckets
- See EPA guidance Page 33: Sample Recordkeeping Form For Liquid Tightness Tests For Spill Buckets And Containment Sumps (For Use By A Qualified Tester)
Note: For temporarily out-of-service UST systems: spill and overfill operation and maintenance testing is not required.
For Triennial Tightness Testing: obtain authorization to discharge wastewater, or use pump-and-haul and keep records to show proper disposal (such as a waste manifest or trip ticket)
If not tested triennially, maintain documentation showing that the spill prevention equipment is double-walled and the integrity of both walls is periodically inspected (note: this option is not applicable to Under-Dispenser Containment (UDC) on new dispensers).

## Slide 15: Periodic Inspection of Overfill Prevention
Overfill Prevention Equipment
  Every 3 years
  Ball float
  Automatic shutoff valve
Notes: Inspect overfill prevention equipment every 3 years to ensure the Automatic Shutoff Device or Ball Float Valve (Flow Restrictor) is set at and will activate at the correct level.

## Slide 16: Periodic Inspection of Overfill Prevention
How do I comply?
UST systems prior to September 1, 2018:
  First 3 year inspection by January 1, 2021
UST systems in use on or after September 1, 2018:
  First 3 year inspection upon startup
Notes: At UST systems in use prior to Sept. 1, 2018: you must conduct your first triennial inspection of overfill prevention equipment by January 1, 2021.
At UST systems in use on or after Sept. 1, 2018: you must conduct your first triennial overfill prevention equipment inspection upon startup.
Keep records for 5 years.
For temporarily out-of-service UST systems: overfill prevention equipment inspections are not required.
See EPA guidance Page 36: Checklist For Automatic Shutoff Devices
See EPA guidance Page 38: Checklist For Overfill Alarms
See EPA guidance Page 40: Checklist For Ball Float Valves
See EPA guidance Page 42: Sample Recordkeeping Form For Overfill Equipment Inspections (For Use By A Qualified Inspector)

## Slide 17: Temporarily Out of Service Tanks
Do not require spill and overfill operation and maintenance walkthrough inspections
Do not require spill and overfill operation and maintenance periodic testing
Notes: Temporarily out-of-service UST systems do not require walkthrough inspections of spill and overfill equipment, or periodic testing of spill and overfill equipment.

## Slide 18: Annual Testing Release Detection
Release Detection Equipment
  Every year
  Tested for proper operation
  Examples: ATG/controllers, alarms, battery backup, ALLD, probes/sensors, vacuum pumps/pressure gauges, etc.
Notes: By January 1, 2021, all new and existing systems must conduct annual release detection equipment testing. This includes:
Automatic tank gauge (ATG)/controllers, alarm, battery backup, automatic line leak detector (ALLD), probes and sensors, vacuum pumps and pressure gauges, hand-held electronic sampling equipment associated with groundwater and vapor monitoring. All of this equipment must be tested for proper operation.
Test method: Petroleum Equipment Institute (PEI) Publication RP1200, "Recommended Practices for the Testing and Verification of Spill, Overfill, Leak Detection and Secondary Containment Equipment at UST Facilities"

## Slide 19: Annual Testing Release Detection
How do I comply?
New and Existing facilities
  First test by January 1, 2021
  Keep records for 5 years
Notes: See EPA guidance Page 10: Sample Annual Release Detection Testing Recordkeeping Form
In addition to the general Sample Annual Release Detection Testing Recordkeeping Form, the EPA guidance includes annual testing checklists for specific release detection methods (Automatic Tank Gauging, Secondary Containment with Interstitial Monitoring, Statistical Inventory Reconciliation, etc.)

## Slide 20: 30-Day Release Detection
Every 30 days
Monitor tanks and piping
Approved method of release detection
Passing results once every 30 days
Notes: Monitor tanks and piping and obtain passing results at least once every 30 days. No longer allowed to go 35 days between passing tests.
- This applies to all facilities, which must comply immediately when the rules are effective.
- This is an EPA requirement and Texas cannot be less stringent than the federal rules.
Obtain passing results at least once every 30 days
- Existing systems must meet 30-day requirement as soon as the new rules are effective.
- New systems must begin complying with 30-day requirement immediately.
Tanks/piping installed on or after Jan. 1, 2009 must use interstitial monitoring as primary release detection method by Sept. 1, 2018.
- This change will make these systems subject to new walkthrough inspection, and periodic testing and inspection requirements.
- This is discussed on the next slide.

## Slide 21: 30-Day Release Detection
How do I comply?
Existing Facilities
  Applies immediately once new rules are effective (May 2018)
New Facilities
  Applies immediately upon startup
Installed after January 1, 2009
  Primary Interstitial Monitoring by September 1, 2018
Notes: If you use Statistical Inventory Reconciliation (SIR) with Inventory Control, you must receive passing results from the SIR vendor within 30 days of the previous passing result. If you can’t, then the procedure cannot be used to comply with the release detection rules.
You may consider testing more frequently than required to ensure you don’t miss the 30-day due date. Set calendar reminders so you don’t forget.
Tanks/piping installed on or after Jan. 1, 2009 must use interstitial monitoring as the primary release detection method by Sept. 1, 2018. This change will make these systems subject to new walkthrough inspection, and periodic testing and inspection requirements.

## Slide 22: Release Detection for Used Oil Tanks
Used oil tanks
  ATG without Inventory Control
  Same exception as emergency generators
Notes: This is the same exemption that is allowed for Emergency Generator Tanks. The current rules allow emergency generators to use ATG as their sole source of tank release detection, without inventory control.
Note: this exemption only applies to tank release detection for these systems. Piping on these systems still must be monitored every 30 days using an approved release detection method.

## Slide 23: Release Detection for Used Oil Tanks
How do I comply?
  Conduct 30 day release detection
  Keep records for 5 years

## Slide 24: Flow Restrictors
Flow restrictors (ball floats) are not allowed when overfill prevention is installed or replaced
Effective September 1, 2018

## Slide 25: Flow Restrictors
How do I comply?
Existing Systems
  Cannot use flow restrictors if repaired or replaced on or after September 1, 2018
New systems built on or after 9/1/18:
  Must use automatic shutoff valve
Keep records of installation and repairs
Notes: Existing systems may continue to use flow restrictors; however, if a repair or replacement is needed after Sept. 1, 2018, flow restrictors may not be used for overfill prevention (an automatic shutoff valve i.e. “flapper valve” would be required instead).

## Slide 26: Repairs
Test within 30 days of repairs to:
  Spill and overfill prevention equipment
  Secondary containment used for interstitial monitoring
Keep records of testing results

## Slide 27: Oil Water Separators
Removed from state rules:
  Operator Training for oil/water separators
    Also removed this requirement for other partially excluded USTs
  Use of registered/licensed personnel to install or permanently remove partially excluded USTs
How do I comply?
No operational changes are needed to comply
Notes: New rules not only remove operator training requirements for oil/water separators, but also for other partially excluded USTs in 30 TAC 334.4.
New rule also removed requirement to use registered/licensed personnel to install and permanently remove oil water separators and other partially excluded USTs in 334.4.

## Slide 28: E10+ and B20+
Prior to switching to E10+ and B20+
  Requires 30 day construction notification
  Submit an agency registration form within 30 days
Notes: These are new requirements for switching to a regulated substance containing greater than 10% ethanol (E10+) or greater than 20% biodiesel (B20+).

## Slide 29: E10+ and B20+
How do I comply?
30 days before switching:
  Submit construction notification to agency
Within 30 days of switching:
  Submit amended UST Registration & Self-Certification Form (TCEQ-0724)

## Slide 30: Operator Training
Certified Class A and Class B operators must be re-trained by January 1, 2020
Must take an Operator Training course that has been submitted and approved by the agency after April 1, 2018
Notes: Certified Class A and Class B operators must be re-trained by January 1, 2020 (notwithstanding the 3-year re-training requirements).
Must take an Operator Training course that is submitted to and approved by the agency after April 1, 2018.
Intent of rule is to require re-training of operators after the new rules become effective so operators can be adequately informed on the new regulations.

## Slide 31: Operator Training
How do I comply?
Re-train Class A and B operators
  Every 3 years
  Agency-approved course for UST Facility Class A and B Operator Training
  Re-training of ALL operators (January 1, 2020)
Notes: Ensure your Class A and B operators are re-trained every 3 years by an agency-approved course for UST Facility Class A and B Operator Training.
By Jan. 1, 2020, re-train Class A and B operators using an approved course that incorporates the new requirements.
To allow training providers time to incorporate the new requirements into their training, the new rules provide a timeline for submission/approval of the course incorporating the new requirements (after April 1, 2018), and a deadline for re-training of all operators (January 1, 2020).
Note: This does not mean that you can allow your Operator Training certification to lapse until 1/1/2020. You still must meet your 3-year re-training date as required, and then be re-trained according to the new rules by 1/1/2020.

## Slide 32: Texas Rulemaking Process
Proposed rules to Commissioner’s Agenda on May 9, 2018
Rules expected to be effective on May 31, 2018
Notes: Reminder: the new requirements have been drafted in the proposed rules, but they are not effective yet. We anticipate they will be approved as drafted. The EPA guidance may help in the meantime while our “UST Compliance Notebook for Texas” guidance is updated to incorporate these new requirements after rule adoption. Disclaimer: use caution when using this EPA guidance because it is based on the Federal rules; TCEQ’s rules must be at least as stringent, but the agency can implement rules that are more stringent than the federal rules.

## Slide 33: Access New Rules & Get Updates
Rules published in Texas Register: 5/25/2018
  Prior to publishing, access pending adoption language at: https://www.tceq.texas.gov/rules/pendadopt.html
  Reference Rule Project No. 2016-019-334-CE
Sign Up for Email Updates:
  https://service.govdelivery.com/accounts/TXTCEQ/subscriber/new
Notes: You can sign up for email updates on specific topics (i.e. Petroleum Storage Tank Rules), or you can subscribe for The Advocate which includes rule updates for all media.

## Slide 34: Thank You!
Rebekah Stanush
Compliance Assistance Specialist
Austin Central Office
512-239-5834
Rebekah.Stanush@tceq.texas.gov
Rebecca Costigan
Compliance Assistance Specialist
Houston Regional Office
713-767-3693
Rebecca.Costigan@tceq.texas.gov

## Slide 35: EPA Guidance
Operating And Maintaining Underground Storage Tank Systems- Practical Help And Checklists (EPA 510-K-16-001, 2/2016)
Page 54: Sample Walkthrough Inspection Checklist
Page 32: Checklist For Spill Buckets
Page 33: Sample Recordkeeping Form For Liquid Tightness Tests For Spill Buckets And Containment Sumps (For Use By A Qualified Tester)
Page 36: Checklist For Automatic Shutoff Devices
Page 38: Checklist For Overfill Alarms
Page 40: Checklist For Ball Float Valves
Page 42: Sample Recordkeeping Form For Overfill Equipment Inspections (For Use By A Qualified Inspector)
Page 10: Sample Annual Release Detection Testing Recordkeeping Form
Notes: EPA guidance available online: https://www.epa.gov/sites/production/files/2016-02/documents/om_final_2-17-16_508_0.pdf
Note: this is not an inclusive list of all the checklists available; there are more checklists in the EPA guidance.